# ANNEX II + III:	 TECHNICAL SPECIFICATIONS + TECHNICAL OFFER

- Contract title: Supply of “Purchase of Energy Storage System”	p 1 / …

Publication reference: BMP1/2.2/2338/2017- 12

Columns 1-2 should be completed by the Contracting Authority

Columns 3-4 should be completed by the tenderer

Column 5 is reserved for the evaluation committee

Annex III - the Contractor's technical offer

The tenderers are requested to complete the template on the next pages:

- Column 2 is completed by the Contracting Authority shows the required specifications (not to be modified by the tenderer),

- Column 3 is to be filled in by the tenderer and must detail what is offered (for example the words “compliant” or “yes” are not sufficient)

- Column 4 allows the tenderer to make comments on its proposed supply and to make eventual references to the documentation

The eventual documentation supplied should clearly indicate (highlight, mark) the models offered and the options included, if any, so that the evaluators can see the exact configuration. Offers that do not permit to identify precisely the models and the specifications may be rejected by the evaluation committee.

The offer must be clear enough to allow the evaluators to make an easy comparison between the requested specifications and the offered specifications.

| 1. Item Number | 2. Specifications Required |  | 3. Specifications Offered | 4. Notes, remarks, ref to documentation | 5. Evaluation Committee’s notes |
| --- | --- | --- | --- | --- | --- |
|  | Description |  |  |  |  |
|  | Battery energy storage system consisted of: |  |  |  |  |
| 1 | Battery energy packs | - Lithium battery; - Total battery capacity of at least 7 kWh; - Battery cycle life of at least 2500 cycles; - Battery pack voltage range of 42~56Vdc; and battery pack discharge/charge current: minimum 250 A; - Working temperature -30~60ºC - Storage temperature -40~55ºC - Working condition moisture 0%~85% - Storage condition moisture 5%~95% - Warranty of at least two years |  |  |  |
| 2 | Inverters | - Total power of at least 3x3 kW - Nominal operating voltage: 720Vdc, Vmax PV 900Vdc; - Nominal operating voltage at Grid/AC output: 230/400Vac; - Nominal operating voltage at AC Input: 230/400Vac, - Nominal operating frequency: 50Hz; - Maximum operating frequency 50Hz; - Battery voltage range: 42~56Vdc, Maximum charging current: 10-200A; - Possibility for selecting a load supply source: PV/Battery/Grid and PV/Grid/Battery; - Possibility for priority setting: Load/Battery/Grid and Load/Battery; - Possibility for selecting a battery charging source: PV and grid and PV only; - Software for PC; - Communication interface: RS-232 and/or RS485 and/or USB - Communication protocol: CAN Interface and/or MODBUS and/or equivalent - Warranty of at least two years |  |  |  |
| 3 | Monitoring system | Hardware features: - Measurement of electricity consumption with following parameters: phase and line voltages, phase currents, active, reactive and apparent power, active and reactive energy, power factor and frequency with a relative measurement uncertainty of less than 1% - Telemetric data transfer and storage via Internet in a minimum interval of 1 min - Installation of equipment in own electrical cabinet with accompanying low voltage switchgear - Technical support and service of equipment Software features: - Dedicated software and lease of a web server for 1 year - The software should be accessible from a PC, tablet or smartphone via Internet - Data storage in a database - Numerical and graphical representation of data - Automatic calculation of the maximum engaged power in an interval of 15 minutes - Possibility of defining a desired load profile and comparison to the actual load profile - Software technical support and maintenance of at least 1 year - Ability to download data in a spreadsheet for additional analysis |  |  |  |
| 4 | Cabinet for battery energy storage system | - Suitable for the battery pack - Should allow secure operation in compliance with the working condition parameters of the battery pack |  |  |  |
| 5 | Electric cabling | - Conductor: Copper wires, according to EN 60228; - Length of at least 400 m; - Insulation: XLPE compound; - Sheath: PVC compound; - Resistance: according to EN 60228; - Operating temperature: 90 ºC; - Overload temperature: 130 ºC/100 h per year; - Short circuit temperature at least 200 ºC (for at least 3 sec.); - Nominal voltage: 0.6/1 kV; |  |  |  |
| 6 | Additional equipment | - Switchgear; - Additional cabinets; - Other equipment necessery for installation to be suitable and appropriate to the system in order to provide safety and security furing its utilization |  |  |  |